## List1
PV modul | Trina TSM-DE06M.08 | Trina TSM-DE06M.08 | Axitec X HC 400 | Axitec X HC 400 | Axitec X HC 400 | gsb 97W | MEPV 156 470W | MEPV 156 470W | Eco Line HC M108/400 |  | Eco Line HC M108/400 | Eco Line HC M108/400 |  | NUJD 540 HC | NUJD 540 HC | NUJD 540 HC | NUJD 540 HC | NUJD 540 HC | NUJD 540 HC | Canad.CS3K | Canad.CS3K | JAM60S20-300 | JAM60S20-301 | JAM60S20-300 | JAM60S20-301 | JKM400N-6RL3-B | JKM400N-6RL3-B | JKM400N-6RL3-B | JKM400N-6RL3-B | JKM400N-6RL3-B | JKM400N-6RL3-B | LG365Q1C 365 | LG365Q1C 365 | LG365Q1C 365 | LG365Q1C 365 | LG365Q1C 365 | LG365Q1C 365 | ECO 500M | ECO 500M | ECO 500M | ECO 500M
| STC* | NMOT** | STC* | STC* | STC* | STC* |  |  | STC | NOCT | STC | STC | NOCT | STC | NMOT | STC | NMOT | STC | NMOT | STC* | NMOT* | STC* | NOCT* | STC* | NOCT* | STC* | NMOT* | STC* | NMOT* | STC* | NMOT* | STC* | NOCT* | STC* | NOCT* | STC* | NOCT* | STC* | NOCT* | STC* | NOCT*
Pn(W) | 330 | 250 | 400 | 400 | 400 | 97 | 470 | 470 | 400 | 296.96 | 400 | 400 | 296.96 | 540 | 404.78 | 540 | 404.78 | 540 | 404.78 | 375 | 280 | 380 | 287 | 380 | 287 | 400 | 302 | 400 | 302 | 400 | 302 | 365 | 275 | 365 | 275 | 365 | 275 | 500 | 404.78 | 500 | 404.78
n | 8 | 8 | 5 | 6 | 7 | 3 | 3 | 6 | 8 | 8 | 9 | 9 | 9 | 7 | 7 | 6 | 6 | 5 | 5 | 6 | 6 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 5 | 5 | 6 | 6 | 6 | 6 | 8 | 8 | 4 | 4 | 4 | 4
p | 2 | 2 | 2 | 2 | 2 | 8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
nxPn(W) | 5280 | 4000 | 4000 | 4800 | 5600 | 2328 | 1410 | 2820 | 3200 | 2375.68 | 3600 | 3600 | 2672.64 | 3780 | 2833.46 | 3240 | 2428.68 | 2700 | 2023.9 | 2250 | 1680 | 3040 | 2296 | 3040 | 2296 | 5600 | 4228 | 2800 | 2114 | 4000 | 3020 | 2190 | 1650 | 2190 | 1650 | 2920 | 2200 | 2000 | 1619.12 | 2000 | 1619.12
Umpp(V) | 33.8 | 31.6 | 41.12 | 41.12 | 41.12 | 75.5 | 44.5 | 44.5 | 31.14 | 28.61 | 31.14 | 31.14 | 28.61 | 41.64 | 38.81 | 41.64 | 38.81 | 41.64 | 38.81 | 34.3 | 32 | 34.77 | 32.72 | 34.77 | 32.72 | 41.7 | 39.6 | 41.7 | 39.6 | 41.7 | 39.6 | 36.7 | 36.6 | 36.7 | 36.6 | 36.7 | 36.6 | 39 | 37.2 | 39 | 37.2
nxUmpp | 270.4 | 252.8 | 205.6 | 246.72 | 287.84 | 226.5 | 133.5 | 267 | 249.12 | 228.88 | 280.26 | 280.26 | 257.49 | 291.48 | 271.67 | 249.84 | 232.86 | 208.2 | 194.05 | 205.8 | 192 | 278.16 | 261.76 | 278.16 | 261.76 | 291.9 | 277.2 | 291.9 | 277.2 | 208.5 | 198 | 220.2 | 219.6 | 220.2 | 219.6 | 293.6 | 292.8 | 156 | 148.8 | 156 | 148.8
Uoc(V) | 40.6 | 38.3 | 48.81 | 48.81 | 48.81 | 99 | 53.5 | 53.5 | 37.08 | 34.24 | 37.08 | 37.08 | 34.24 | 50.43 | 47.71 | 50.43 | 47.71 | 50.43 | 47.71 | 39.7 | 37.2 | 41.62 | 39.14 | 41.62 | 39.14 | 49.8 | 48.5 | 49.8 | 48.5 | 49.8 | 48.5 | 42.8 | 40.2 | 42.8 | 40.2 | 42.8 | 40.2 | 46.8 | 44.6 | 46.8 | 44.6
nxUoc(V) | 324.8 | 306.4 | 244.05 | 292.86 | 341.67 | 297 | 160.5 | 321 | 296.64 | 273.92 | 333.72 | 333.72 | 308.16 | 353.01 | 333.97 | 302.58 | 286.26 | 252.15 | 238.55 | 238.2 | 223.2 | 332.96 | 313.12 | 332.96 | 313.12 | 348.6 | 339.5 | 348.6 | 339.5 | 249 | 242.5 | 256.8 | 241.2 | 256.8 | 241.2 | 342.4 | 321.6 | 187.2 | 178.4 | 187.2 | 178.4
number of cells | 60 | 60 | 72 | 72 | 72 | amorph | 156 | 156 | 108 | 108 | 108 | 108 | 108 | 144 | 144 | 144 | 144 | 144 | 144 | 120 | 120 | 120 | 120 | 120 | 120 | 144 | 144 | 144 | 144 | 144 | 144 | 120 | 120 | 120 | 120 | 120 | 120 | 144 | 144 | 144 | 144
Ktu(%/K) | -0.26 | -0.26 | -0.29 | -0.29 | -0.29 | -0.42 | -0.28 | -0.28 | -0.285 | -0.285 | -0.285 | -0.285 | -0.285 | -0.26 | -0.26 | -0.26 | -0.26 | -0.26 | -0.26 | -0.27 | -0.27 | -0.27 | -0.27 | -0.27 | -0.27 | -0.29 | -0.29 | -0.29 | -0.29 | -0.29 | -0.29 | -0.24 | -0.24 | -0.24 | -0.24 | -0.24 | -0.24 | -0.27 | -0.27 | -0.27 | -0.27
Ktu(V/K) | -0.10556 | -0.09958 | -0.14155 | -0.14155 | -0.14155 | -0.4158 | -0.1498 | -0.1498 | -0.10568 | -0.097584 | -0.10568 | -0.10568 | -0.097584 | -0.13112 | -0.12405 | -0.13112 | -0.12405 | -0.13112 | -0.12405 | -0.10719 | -0.10044 | -0.11237 | -0.10568 | -0.11237 | -0.10568 | -0.14442 | -0.14065 | -0.14442 | -0.14065 | -0.14442 | -0.14065 | -0.10272 | -0.09648 | -0.10272 | -0.09648 | -0.10272 | -0.09648 | -0.13112 | -0.12405 | -0.13112 | -0.12405
Uoc(-25°C)(V) | 45.878 | 43.279 | 55.8875 | 55.8875 | 55.8875 | 119.79 | 60.99 | 60.99 | 42.3639 | 39.1192 | 42.3639 | 42.3639 | 39.1192 | 56.9859 | 53.9123 | 56.9859 | 53.9123 | 56.9859 | 53.9123 | 45.0595 | 42.222 | 47.2387 | 44.4239 | 47.2387 | 44.4239 | 57.021 | 55.5325 | 57.021 | 55.5325 | 57.021 | 55.5325 | 47.936 | 45.024 | 47.936 | 45.024 | 47.936 | 45.024 | 56.9859 | 53.9123 | 56.9859 | 53.9123
nxUoc(-25°C)(V) | 367.024 | 346.232 | 279.4373 | 335.3247 | 391.2122 | 359.37 | 182.97 | 365.94 | 338.9112 | 312.9536 | 381.2751 | 381.2751 | 352.0728 | 398.9013 | 377.3861 | 341.9154 | 323.4738 | 284.9295 | 269.5615 | 270.357 | 253.332 | 377.9096 | 355.3912 | 377.9096 | 355.3912 | 399.147 | 388.7275 | 399.147 | 388.7275 | 285.105 | 277.6625 | 287.616 | 270.144 | 287.616 | 270.144 | 383.488 | 360.192 | 341.9154 | 323.4738 | 341.9154 | 323.4738
Umpp(-25°C) | 39.078 | 36.579 | 48.1974 | 48.1974 | 48.1974 | 96.29 | 51.99 | 51.99 | 36.4239 | 33.4892 | 36.4239 | 36.4239 | 33.4892 | 48.1959 | 45.0123 | 48.1959 | 45.0123 | 48.1959 | 45.0123 | 39.6595 | 37.022 | 40.3887 | 38.0039 | 40.3887 | 38.0039 | 48.921 | 46.6325 | 48.921 | 46.6325 | 48.921 | 46.6325 | 41.836 | 41.424 | 41.836 | 41.424 | 41.836 | 41.424 | 48.1959 | 45.0123 | 48.1959 | 45.0123
nxUmpp(-25°C) | 312.624 | 292.632 | 240.9872 | 289.1847 | 337.3821 | 288.87 | 155.97 | 311.94 | 291.3912 | 267.9136 | 327.8151 | 327.8151 | 301.4028 | 337.3713 | 315.0861 | 289.1754 | 270.0738 | 240.9795 | 225.0615 | 237.957 | 222.132 | 323.1096 | 304.0312 | 323.1096 | 304.0312 | 342.447 | 326.4275 | 342.447 | 326.4275 | 244.605 | 233.1625 | 251.016 | 248.544 | 251.016 | 248.544 | 334.688 | 331.392 | 192.7836 | 180.0492 | 192.7836 | 180.0492
Umpp(+75°C)(V) | 28.522 | 26.621 | 34.0425 | 34.0425 | 34.0425 | 54.71 | 37.01 | 37.01 | 25.8561 | 23.7308 | 25.8561 | 25.8561 | 23.7308 | 35.0841 | 32.6077 | 35.0841 | 32.6077 | 35.0841 | 32.6077 | 28.9405 | 26.978 | 29.1513 | 27.4361 | 29.1513 | 27.4361 | 34.479 | 32.5675 | 34.479 | 32.5675 | 34.479 | 32.5675 | 31.564 | 31.776 | 31.564 | 31.776 | 31.564 | 31.776 | 32.4441 | 30.9977 | 32.4441 | 30.9977
nxUmpp(+75°C)(V) | 228.176 | 212.968 | 170.2127 | 204.2553 | 238.2978 | 164.13 | 111.03 | 222.06 | 206.8488 | 189.8464 | 232.7049 | 232.7049 | 213.5772 | 245.5887 | 228.2539 | 210.5046 | 195.6462 | 175.4205 | 163.0385 | 173.643 | 161.868 | 233.2104 | 219.4888 | 233.2104 | 219.4888 | 241.353 | 227.9725 | 241.353 | 227.9725 | 172.395 | 162.8375 | 189.384 | 190.656 | 189.384 | 190.656 | 252.512 | 254.208 | 129.7764 | 123.9908 | 129.7764 | 123.9908
Impp(A) | 9.76 | 7.91 | 9.74 | 9.74 | 9.74 | 1.29 | 10.57 | 10.57 | 12.85 | 10.38 | 12.85 | 12.85 | 10.38 | 12.97 | 10.43 | 12.97 | 10.43 | 12.97 | 10.43 | 9.53 | 8.75 | 10.93 | 8.78 | 10.93 | 8.78 | 9.6 | 7.66 | 9.6 | 7.66 | 9.6 | 7.66 | 9.6 | 7.51 | 9.6 | 7.51 | 9.6 | 7.51 | 12.82 | 10.13 | 12.82 | 10.13
Isc (A) | 10.39 | 8.36 | 10.46 | 10.46 | 10.46 | 1.6 | 11.04 | 11.04 | 13.57 | 10.96 | 13.57 | 13.57 | 10.96 | 13.66 | 11.06 | 13.66 | 11.06 | 13.66 | 11.06 | 11.61 | 9.37 | 11.47 | 9.3 | 11.47 | 9.3 | 12.28 | 9.9 | 12.28 | 9.9 | 12.28 | 9.9 | 10.8 | 8.7 | 10.8 | 8.7 | 10.8 | 8.7 | 13.4 | 10.81 | 13.4 | 10.81
pxImpp(A) | 20.78 | 16.72 | 20.92 | 20.92 | 20.92 | 12.8 | 11.04 | 11.04 | 13.57 | 10.96 | 13.57 | 13.57 | 10.96 | 13.66 | 11.06 | 13.66 | 11.06 | 13.66 | 11.06 | 9.53 | 8.75 | 10.75 | 8.78 | 10.75 | 8.78 | 19.2 | 15.32 | 9.6 | 7.66 | 19.2 | 15.32 | 9.6 | 7.51 | 9.6 | 7.51 | 9.6 | 7.51 | 12.82 | 10.13 | 12.82 | 10.13
Kti(%/K) | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.06 | 0.049 | 0.049 | 0.049 | 0.049 | 0.049 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.054 | 0.05 | 0.05 | 0.044 | 0.05 | 0.044 | 0.05 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.048 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
Kti(A/K) | 0.003904 | 0.003164 | 0.003896 | 0.003896 | 0.003896 | 0.000774 | 0.006342 | 0.006342 | 0.0062965 | 0.0050862 | 0.0062965 | 0.0062965 | 0.0050862 | 0.0070038 | 0.0056322 | 0.0070038 | 0.0056322 | 0.0070038 | 0.0056322 | 0.004765 | 0.004375 | 0.0048092 | 0.00439 | 0.0048092 | 0.00439 | 0.004608 | 0.0036768 | 0.004608 | 0.0036768 | 0.004608 | 0.0036768 | 0.00384 | 0.003004 | 0.00384 | 0.003004 | 0.00384 | 0.003004 | 0.005128 | 0.004052 | 0.005128 | 0.004052
Impp(75°C)(A) | 9.9552 | 8.0682 | 9.9348 | 9.9348 | 9.9348 | 1.3287 | 10.8871 | 10.8871 | 13.1648 | 10.6343 | 13.1648 | 13.1648 | 10.6343 | 13.3202 | 10.7116 | 13.3202 | 10.7116 | 13.3202 | 10.7116 | 9.7683 | 8.9688 | 11.1705 | 8.9995 | 11.1705 | 8.9995 | 9.8304 | 7.8438 | 9.8304 | 7.8438 | 9.8304 | 7.8438 | 9.792 | 7.6602 | 9.792 | 7.6602 | 9.792 | 7.6602 | 13.0764 | 10.3326 | 13.0764 | 10.3326
pxImpp(75°C)(A) | 19.9104 | 16.1364 | 19.8696 | 19.8696 | 19.8696 | 10.6296 | 10.8871 | 10.8871 | 13.1648 | 10.6343 | 13.1648 | 13.1648 | 10.6343 | 13.3202 | 10.7116 | 13.3202 | 10.7116 | 13.3202 | 10.7116 | 9.7683 | 8.9688 | 11.1705 | 8.9995 | 11.1705 | 8.9995 | 19.6608 | 15.6877 | 9.8304 | 7.8438 | 19.6608 | 15.6877 | 9.792 | 7.6602 | 9.792 | 7.6602 | 9.792 | 7.6602 | 13.0764 | 10.3326 | 13.0764 | 10.3326
Pmpp(75°C)(W) | 283.9422 | 214.7836 | 338.2059 | 338.2059 | 338.2059 | 72.6932 | 402.9316 | 402.9316 | 340.391 | 252.3607 | 340.391 | 340.391 | 252.3607 | 467.3269 | 349.281 | 467.3269 | 349.281 | 467.3269 | 349.281 | 282.698 | 241.9589 | 325.6334 | 246.9112 | 325.6334 | 246.9112 | 338.9424 | 255.4543 | 338.9424 | 255.4543 | 338.9424 | 255.4543 | 309.0747 | 243.4105 | 309.0747 | 243.4105 | 309.0747 | 243.4105 | 424.252 | 320.2868 | 424.252 | 320.2868
pxnxPmpp(75°C)(W) | 4543.0754 | 3436.5368 | 3382.0593 | 4058.4711 | 4734.883 | 1744.6362 | 1208.7947 | 2417.5894 | 2723.1283 | 2018.8855 | 3063.5193 | 3063.5193 | 2271.2462 | 3271.2881 | 2444.9668 | 2803.9613 | 2095.6858 | 2336.6344 | 1746.4048 | 1696.1882 | 1451.7536 | 2605.0674 | 1975.2895 | 2605.0674 | 1975.2895 | 4745.1931 | 3576.3596 | 2372.5965 | 1788.1798 | 3389.4236 | 2554.5426 | 1854.4481 | 1460.4631 | 1854.4481 | 1460.4631 | 2472.5975 | 1947.2841 | 1697.0081 | 1281.1473 | 1697.0081 | 1281.1473
Electric heater
rated heater power (W) | 4500 | 4500 | 3000 | 4000 | 4000 | 4000 | 2000 | 3000 | 3000 | 3000 | 3000 | 4000 | 3000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 2860 | 2860 | 1500 | 1500 | 800 | 800 | 5000 | 5000 | 3000 | 3000 | 5000 | 5000 | 2000 | 2000 | 3000 | 3000 | 3000 | 3000 | 5000 | 5000 | 5500 | 5500
rated heater current (A) | 19.5652 | 19.5652 | 13.0435 | 17.3913 | 17.3913 | 17.3913 | 16.6667 | 13.0435 | 13.0435 | 13.0435 | 13.0435 | 17.3913 | 13.0435 | 17.3913 | 17.3913 | 17.3913 | 17.3913 | 17.3913 | 17.3913 | 12.4348 | 12.4348 | 6.5217 | 6.5217 | 3.4783 | 3.4783 | 21.7391 | 21.7391 | 13.0435 | 13.0435 | 21.7391 | 21.7391 | 8.6957 | 8.6957 | 13.0435 | 13.0435 | 13.0435 | 13.0435 | 21.7391 | 21.7391 | 23.913 | 23.913
heater resistance (Ohm) | 11.7556 | 11.7556 | 17.6333 | 13.225 | 13.225 | 13.225 | 7.2 | 17.6333 | 17.6333 | 17.6333 | 17.6333 | 13.225 | 17.6333 | 13.225 | 13.225 | 13.225 | 13.225 | 13.225 | 13.225 | 18.4965 | 18.4965 | 35.2667 | 35.2667 | 66.125 | 66.125 | 10.58 | 10.58 | 17.6333 | 17.6333 | 10.58 | 10.58 | 26.45 | 26.45 | 17.6333 | 17.6333 | 17.6333 | 17.6333 | 10.58 | 10.58 | 9.6182 | 9.6182
max output current (A) | 19.4101 | 18.1164 | 9.6529 | 15.4446 | 18.0187 | 12.4106 | 15.4208 | 12.5932 | 11.7306 | 10.7663 | 13.1969 | 17.5958 | 12.1121 | 18.57 | 17.2593 | 15.9172 | 14.7937 | 13.2643 | 12.3281 | 9.3879 | 8.7513 | 6.6128 | 6.2237 | 3.5268 | 3.3193 | 22.8122 | 21.5475 | 13.6873 | 12.9285 | 16.2944 | 15.3911 | 7.1601 | 7.2082 | 10.7401 | 10.8122 | 14.3202 | 14.4163 | 12.2662 | 11.7194 | 13.4928 | 12.8913
possible heater power (W) at Umpp (+ 75 ° C) | 4428.9091 | 3858.2072 | 1643.0461 | 3154.6486 | 4293.8272 | 2036.9495 | 1712.1751 | 2796.4448 | 2426.4514 | 2043.9502 | 3070.9775 | 4094.6367 | 2586.8745 | 4560.5905 | 3939.4966 | 3350.6379 | 2894.3241 | 2326.8319 | 2009.9473 | 1630.1401 | 1416.5515 | 1542.167 | 1366.0302 | 822.4891 | 728.5495 | 5505.7912 | 4912.2364 | 3303.4747 | 2947.3418 | 2809.0771 | 2506.243 | 1356.0038 | 1374.2802 | 2034.0056 | 2061.4202 | 3616.01 | 3664.7471 | 1591.8633 | 1453.0925 | 1751.0497 | 1598.4017
real power (W) at Umpp (+ 75° C) | 4428.9091 | 3436.5368 | 1643.0461 | 3154.6486 | 4000 | 1744.6362 | 1208.7947 | 2417.5894 | 2426.4514 | 2018.8855 | 3000 | 3063.5193 | 2271.2462 | 3271.2881 | 2444.9668 | 2803.9613 | 2095.6858 | 2326.8319 | 1746.4048 | 1630.1401 | 1416.5515 | 1500 | 1366.0302 | 800 | 728.5495 | 4745.1931 | 3576.3596 | 2372.5965 | 1788.1798 | 2809.0771 | 2506.243 | 1356.0038 | 1374.2802 | 1854.4481 | 1460.4631 | 2472.5975 | 1947.2841 | 1591.8633 | 1281.1473 | 1697.0081 | 1281.1473
The power in row 35 should be greater or not much less than the power in row 29
The data is entered into green colored cells
Pn (W) - rated power of PV module
n is the number of series connected modules in string
p-number of strings
nxPn (W) -total power
Umpp (V) -voltage at the point of maximum power
nxUmpp-voltage at the point of maximum generator power
Uoc (V) -voltage of open terminals of each PV module
nxUoc (V) -voltage of open generator terminals
Ktu (% / K) -temperature voltage coefficient
Ktu (V / K) -temperature voltage coefficient
Uoc (-25 ° C) (V) -voltage of open terminals of PV module at -25 ° C
nxUoc (-25 ° C) (V) -voltage of open generator terminals at -25C
nxUmpp (-25 ° C) -voltage at the point of maximum power of the generator at -25 ° C
Impp (W) -current at the point of rated power
Kti (% / K) - temperature current coefficient
Kti (A / K) - temperature current coefficient
*STC: Irradiance 1000W/m2, Cell Temperature 25°C, Air Mass AM1.5
**NMOT: Irradiance at 800W/m2, Ambient Temperature 20°C, Wind Speed 1m/s.